## Sheet1
Below line 7 paste your setup to populate the range read into Rhino as the space attrs library
Y/N | Space Name | Activity | OCC-SCHEDULE | LIGHTING-SCHEDULE | EQUIP-SCHEDULE | EPD W/SF | LPD W/SF | Occupancy SF/PER | MIN-FLOW-RATIO | ACH | OA/Per | OA/SF | MIN-FLOW/SF | DESIGN-HEAT-Temp | HEAT-TEMP-SCH | DESIGN-COOL-Temp | COOL-TEMP-SCH | Space Name | Activity | OCC-SCHEDULE | LIGHTING-SCHEDULE | EQUIP-SCHEDULE | EPD W/SF | LPD W/SF | Occupancy SF/PER | MIN-FLOW-RATIO | ACH | OA/Per | OA/SF | MIN-FLOW/SF | DESIGN-HEAT-Temp | HEAT-TEMP-SCH | DESIGN-COOL-Temp | COOL-TEMP-SCH
Mixed Labs and Offices
1 | Autoclave | aclv | Occ 16/5 CtA Sch | Ltg 16/5 Const A Sch | Ltg 16/5 Const A Sch | 9 | 0.2 | 40 | no_default | no_default |  |  | 1.2 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
1 | Breakroom | brkm | Occ 16/5 Inter Sch | Ltg 16/5 Inter Sch | Misc 16/5 Inter Sch | 0.5 | 0.5 | 40 | no_default | no_default |  |  | 0.4 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
1 | Class | clas | Occ 16/5 Inter Sch | Ltg 16/5 Inter Sch | Misc 16/5 Inter Sch | 0.5 | 0.5 | 40 | no_default | no_default |  |  | 1.4 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
1 | Clean-Room | clea | Occ 16/5 Inter Sch | Ltg 16/5 Const A Sch | 24/5 (low) Sch | 9 | 0.5 | 40 | no_default | no_default |  |  | 1.2 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
1 | Computational | cptr | Occ 16/5 CtA Sch | Ltg 16/5 Const A Sch | Misc 16/5 Const A Sch | 0.5 | 0.5 | 100 | no_default | no_default |  |  | 0.4 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
1 | Conference | conf | Occ 16/5 Inter Sch | Ltg 16/5 Inter Sch | Misc 16/5 Inter Sch | 1 | 0.5 | 20 | no_default | no_default |  |  | 0.4 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
1 | Corridor | corr | Occ 16/5 Inter Sch | Ltg 16/5 Inter Sch | Misc 16/5 Inter Sch | 0 | 0.5 | 250 | no_default | no_default |  |  | 0.4 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
1 | Custodian | cust | Occ 16/5 Inter Sch | Ltg 16/5 Inter Sch | Misc 16/5 Inter Sch | 0 | 0.5 | 200 | no_default | no_default |  |  | 0.4 | 60 | Heating 60 | 80 | Cooling 80
1 | Electrical | elec | 24/5 (low) Sch | 24/5 (low) Sch | 24/5 (mid-high) Sch | 5 | 0.5 | 400 | no_default | no_default |  |  | 0 | 60 | Heating 60 | 80 | Cooling 80
1 | Fume-Hood | fmhd | Occ 16/5 CtA Sch | Ltg 16/5 Const A Sch | 24/5 (low-mid) Sch | 6 | 0.5 | 40 | no_default | no_default |  |  | 1.2 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
1 | Kitchenette | kitc | Occ 16/5 Inter Sch | Ltg 16/5 Inter Sch | Misc 16/5 Inter Sch | 3 | 0.5 | 50 | no_default | no_default |  |  | 0.4 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
1 | Lab | labs | Occ 16/5 CtA Sch | Ltg 16/5 Const A Sch | 24/5 (low-mid) Sch | 6 | 0.5 | 40 | no_default | no_default |  |  | 1.2 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
1 | Lab-Corridor | lcor | Occ 16/5 CtA Sch | Ltg 16/5 Const A Sch | 24/5 (low-mid) Sch | 0 | 0.5 | 200 | no_default | no_default |  |  | 1.2 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
1 | Lab-Support | lbsp | Occ 16/5 CtA Sch | Ltg 16/5 Const A Sch | 24/5 (low-mid) Sch | 9 | 0.5 | 40 | no_default | no_default |  |  | 1.2 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
1 | Mechanical | mech | 24/5 (low) Sch | 24/5 (low) Sch | 24/5 (low-mid) Sch | 5 | 0.5 | 400 | no_default | no_default |  |  | 0 | 60 | Heating 60 | 80 | Cooling 80
1 | Microscope | micr | Occ 16/5 CtA Sch | Ltg 16/5 Const A Sch | 24/5 (low-mid) Sch | 9 | 0.6 | 40 | no_default | no_default |  |  | 1.2 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
1 | Microstomes | mics | Occ 16/5 CtA Sch | Ltg 16/5 Const A Sch | 24/5 (low-mid) Sch | 9 | 0.6 | 40 | no_default | no_default |  |  | 1.2 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
1 | Office | offi | Office Occ A Sch | Office Ltg A Sch | Office Eqp A Sch | 0.5 | 0.5 | 100 | no_default | no_default |  |  | 0.2 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
1 | ShowerRoom | shrm | Occ 16/5 Inter Sch | Ltg 16/5 Inter Sch | Misc 16/5 Inter Sch | 0 | 0.9 | 100 | no_default | no_default |  |  | 0.5 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
1 | Stairs | stai | Occ 16/5 Inter Sch | Occ 16/5 Inter Sch | Misc 16/5 Inter Sch | 0 | 0.9 | 400 | no_default | no_default |  |  | 0 | 60 | Heating 60 | 999 | Cooling 999
1 | Storage | stor | Occ 16/5 Inter Sch | Occ 16/5 Inter Sch | Misc 16/5 Inter Sch | 0 | 0.9 | 200 | no_default | no_default |  |  | 0.4 | 60 | Heating 60 | 80 | Cooling 80
1 | Storage-Equipment | steq | Occ 16/5 CtA Sch | Ltg 16/5 Const A Sch | 24/5 (low-mid) Sch | 12 | 0.9 | 40 | no_default | no_default |  |  | 1.2 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
1 | TeleData | data | 24/5 (low) Sch | 24/5 (low) Sch | 24/5 (mid-high) Sch | 5 | 0.9 | 400 | no_default | no_default |  |  | 0 | 60 | Heating 60 | 80 | Cooling 80
1 | Tissue-Cultures | tcul | Occ 16/5 CtA Sch | Ltg 16/5 Const A Sch | 24/5 (low-mid) Sch | 6 | 0.9 | 40 | no_default | no_default |  |  | 1.2 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
1 | Toilets | toil | 24/5 (high) Sch | 24/5 (mid-high) Sch | Misc 16/5 Inter Sch | 0 | 0.9 | 100 | no_default | no_default |  |  | 0.5 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
1 | Vestibules | vest | 24/5 (mid-high) Sch | 24/5 (low-mid) Sch | Ltg 16/5 Inter Sch | 0 | 0.9 | 200 | no_default | no_default |  |  | 0 | 60 | Heating 60 | 80 | Cooling 80
1 | WriteUp | wrtp | Office Occ A Sch | Office Ltg A Sch | Office Eqp A Sch | 0.5 | 0.9 | 100 | no_default | no_default |  |  | 0.4 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
1 | default | default | Occ 16/5 Const Sch | Ltg 16/5 Const Sch | Misc 16/5 Const Sch | 0 | 0 | 400 | no_default | no_default |  |  | no_default | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
Hospitals
| Clean Holding | clea | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 0.5 | 0.9 | 200 | no_default | no_default |  |  | 0.6 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Conference | conf | Occ 16/7 Intermit Sch | Ltg 16/7 Intermit Sch | Misc 16/7 Intermit Sch | 2 | 0.9 | 20 | 0.3 | no_default |  |  | no_default | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Consultation | cons | Occ 16/7 Intermit Sch | Ltg 16/7 Intermit Sch | Misc 16/7 Intermit Sch | 2 | 0.9 | 20 | 0.3 | no_default |  |  | no_default | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Control | ctrl | Occ 16/7 Intermit Sch | Ltg 16/7 Intermit Sch | Misc 16/7 Intermit Sch | 2 | 0.9 | 100 | no_default | no_default |  |  | no_default | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Copy | copy | 24/7 (low-mid) Sch | 24/7 (mid-high) Sch | 24/7 (low-mid) Sch | 4 | 0.9 | 200 | 0.3 | no_default |  |  | no_default | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Corridor | corr | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 0.1 | 0.9 | 250 | no_default | no_default |  |  | 0.35 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Dining | dini | Occ 16/7 Intermit Sch | Ltg 16/7 Intermit Sch | Misc 16/7 Intermit Sch | 0.5 | 0.9 | 20 | 0.3 | no_default |  |  | no_default | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Electrical | elec | 24/7 (low) Sch | 24/7 (low-mid) Sch | 24/7 (low-mid) Sch | 10 | 0.9 | 400 | 1 | no_default |  |  | 0.4 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Elevator Lobby | elob | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 0.1 | 0.9 | 100 | 0.3 | no_default |  |  | no_default | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Emergency Waiting | ewai | 24/7 (low-mid) Sch | 24/7 (mid-high) Sch | 24/7 (low-mid) Sch | 1 | 0.9 | 25 | no_default | no_default |  |  | 2 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Exam Room | exam | Occ 16/7 Constant Sch | Ltg 16/7 Constant Sch | Misc 16/7 Constant Sch | 3 | 0.9 | 100 | no_default | no_default |  |  | 0.9 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Fitness | fitn | Occ 16/7 Intermit Sch | Ltg 16/7 Intermit Sch | Misc 16/7 Intermit Sch | 4 | 0.9 | 35 | no_default | no_default |  |  | no_default | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Hazardous Storage | hazs | 24/7 (low) Sch | 24/7 (low-mid) Sch | 24/7 (low) Sch | 0.5 | 0.9 | 400 | no_default | no_default |  |  | 1.8 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Housekeeping | hskp | 24/7 (low) Sch | 24/7 (low-mid) Sch | 24/7 (low-mid) Sch | 0.25 | 0.9 | 400 | no_default | no_default |  |  | no_default | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| ICUA | icua | Occ Patient (Avg) Sch | Ltg Patient (Avg) Sch | Misc Patient (Avg) Sch | 5 | 0.9 | 100 | no_default | no_default |  |  | 0.9 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| ICUB | icub | Occ Patient (Peak) Sch | Ltg Patient (Peak) Sch | Misc Patient (Peak) Sch | 5 | 0.9 | 100 | no_default | no_default |  |  | 0.9 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| ICUC | icuc | Occ Patient (Unoc) Sch | Ltg Patient (Unoc) Sch | Misc Patient (Unoc) Sch | 5 | 0.9 | 100 | no_default | no_default |  |  | 0.9 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Imaging | imag | Occ 16/7 Intermit Sch | Ltg 16/7 Intermit Sch | Misc 16/7 Intermit Sch | 10 | 0.9 | 100 | no_default | no_default |  |  | 1.8 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Imaging Equipment | imeq | 24/7 (low) Sch | 24/7 (low-mid) Sch | Misc 16/7 Intermit Sch | 45 | 0.9 | 400 | no_default | no_default |  |  | 0.4 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Kitchen | kitc | Occ 16/7 Intermit Sch | Ltg 16/7 Intermit Sch | Misc 16/7 Intermit Sch | 4 | 0.9 | 50 | no_default | no_default |  |  | 1.2 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Laboratory | labs | Occ 16/7 Constant Sch | Ltg 16/7 Constant Sch | Misc 16/7 Constant Sch | 6 | 0.9 | 100 | no_default | no_default |  |  | 0.9 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Laundry | laun | 24/7 (low-mid) Sch | 24/7 (low-mid) Sch | 24/7 (low-mid) Sch | 10 | 0.9 | 200 | no_default | no_default |  |  | 0.9 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Lobby | lobb | 24/7 (low-mid) Sch | 24/7 (mid-high) Sch | 24/7 (low-mid) Sch | 0.25 | 0.9 | 35 | 0.3 | no_default |  |  | no_default | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Locker | lock | Occ 16/7 Intermit Sch | Ltg 16/7 Intermit Sch | Misc 16/7 Intermit Sch | 0.5 | 0.9 | 200 | no_default | no_default |  |  | 0.9 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Lounge | loun | Occ 16/7 Intermit Sch | Ltg 16/7 Intermit Sch | Misc 16/7 Intermit Sch | 3 | 0.9 | 35 | 0.3 | no_default |  |  | no_default | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Mail | mail | Occ 16/7 Constant Sch | Ltg 16/7 Constant Sch | Misc 16/7 Constant Sch | 2 | 0.9 | 100 | no_default | no_default |  |  | no_default | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Mechanical | mech | 24/7 (low-mid) Sch | 24/7 (mid-high) Sch | 24/7 (low-mid) Sch | 0.5 | 0.9 | 400 | 1 | no_default |  |  | 0.4 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Medication | meds | 24/7 (low-mid) Sch | 24/7 (low-mid) Sch | 24/7 (low-mid) Sch | 4 | 0.9 | 100 | no_default | no_default |  |  | 0.6 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Nourishment | nour | 24/7 (low-mid) Sch | 24/7 (low-mid) Sch | 24/7 (low-mid) Sch | 4 | 0.9 | 100 | no_default | no_default |  |  | 0.6 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Nurse Station | nurs | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 6 | 0.9 | 50 | no_default | no_default |  |  | 0.6 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Office | offi | Occ 16/7 Constant Sch | Ltg 16/7 Constant Sch | Misc 16/7 Constant Sch | 2 | 0.9 | 100 | 0.3 | no_default |  |  | no_default | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| On Call | onca | Occ Patient (Avg) Sch | Ltg Patient (Avg) Sch | Misc Patient (Avg) Sch | 2 | 0.9 | 100 | 0.3 | no_default |  |  | no_default | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Operating Room A | opra | Occ OR A Sch | Ltg OR A Sch | Misc OR A Sch | 8 | 0.9 | 75 | no_default | no_default |  |  | 4 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Operating Room B | oprb | Occ OR B Sch | Ltg OR B Sch | Misc OR B Sch | 8 | 0.9 | 75 | no_default | no_default |  |  | 4 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Patient (Average) | pata | Occ Patient (Avg) Sch | Ltg Patient (Avg) Sch | Misc Patient (Avg) Sch | 3 | 0.9 | 100 | no_default | no_default |  |  | 0.9 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Patient (High) | path | Occ Patient (Peak) Sch | Ltg Patient (Peak) Sch | Misc Patient (Peak) Sch | 3 | 0.9 | 100 | no_default | no_default |  |  | 0.9 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Patient (ICU) | icup | Occ Patient (Avg) Sch | Ltg Patient (Avg) Sch | Misc Patient (Avg) Sch | 5 | 0.9 | 100 | no_default | no_default |  |  | 0.9 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Patient (Isolation) | isop | Occ Patient (Avg) Sch | Ltg Patient (Avg) Sch | Misc Patient (Avg) Sch | 3 | 0.9 | 100 | no_default | no_default |  |  | 1.8 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Patient (Unocc) | patu | Occ Patient (Unoc) Sch | Ltg Patient (Unoc) Sch | Misc Patient (Unoc) Sch | 3 | 0.9 | 100 | no_default | no_default |  |  | 0.9 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Pharmacy | phar | Occ 16/7 Constant Sch | Ltg 16/7 Constant Sch | Misc 16/7 Constant Sch | 3 | 0.9 | 100 | no_default | no_default |  |  | 1.8 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| PROC | proc | Occ 16/7 Constant Sch | Ltg 16/7 Constant Sch | Misc 16/7 Constant Sch | 12 | 0.9 | 35 | no_default | no_default |  |  | 2.5 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Reception | rece | Occ 16/7 Intermit Sch | Ltg 16/7 Intermit Sch | Misc 16/7 Intermit Sch | 0.5 | 0.9 | 35 | no_default | no_default |  |  | no_default | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Receiving | recv | Occ 16/7 Intermit Sch | Ltg 16/7 Intermit Sch | Misc 16/7 Intermit Sch | 4 | 0.9 | 200 | no_default | no_default |  |  | 0.4 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Retail | reta | Occ 16/7 Intermit Sch | 24/7 (mid-high) Sch | Misc 16/7 Intermit Sch | 0.5 | 0.9 | 65 | 0.3 | no_default |  |  | no_default | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Soiled Holding | soil | 24/7 (low-mid) Sch | 24/7 (low-mid) Sch | 24/7 (low-mid) Sch | 0.5 | 0.9 | 200 | no_default | no_default |  |  | 0.6 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Stairs | stai | 24/7 (low) Sch | 24/7 (high) Sch | Misc 16/7 Intermit Sch | 0 | 0.9 | 400 | 1 | no_default |  |  | no_default | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Sterile Storage | ster | Occ 16/7 Constant Sch | Ltg 16/7 Constant Sch | Misc 16/7 Constant Sch | 15 | 0.9 | 100 | no_default | no_default |  |  | no_default | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Sterile Core | core | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 0.5 | 0.9 | 250 | no_default | no_default |  |  | 1 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Storage | stor | 24/7 (low) Sch | 24/7 (low-mid) Sch | 24/7 (low) Sch | 0.5 | 0.9 | 400 | no_default | no_default |  |  | 0.6 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Tel Data | data | 24/7 (low) Sch | 24/7 (low-mid) Sch | 24/7 (low-mid) Sch | 25 | 0.9 | 400 | 1 | no_default |  |  | 0.4 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Toilets | toil | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 0 | 0.9 | 200 | no_default | no_default |  |  | 0.9 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Trash | tras | 24/7 (low-mid) Sch | 24/7 (mid-high) Sch | 24/7 (low-mid) Sch | 0.25 | 0.9 | 400 | no_default | no_default |  |  | 1.8 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Treatment | trea | Occ 16/7 Constant Sch | Ltg 16/7 Constant Sch | Misc 16/7 Constant Sch | 4 | 0.9 | 35 | no_default | no_default |  |  | 2.5 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Triage | tria | Occ Patient (Avg) Sch | Ltg Patient (Avg) Sch | Misc Patient (Avg) Sch | 3 | 0.9 | 100 | no_default | no_default |  |  | 2 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Vestibule | vest | 24/7 (mid-high) Sch | 24/7 (high) Sch | 24/7 (low) Sch | 0 | 0.9 | 200 | 1 | no_default |  |  | 0.4 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Waiting | wait | 24/7 (low-mid) Sch | 24/7 (mid-high) Sch | 24/7 (low-mid) Sch | 1 | 0.9 | 25 | no_default | no_default |  |  | 1 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Workroom | wkrm | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 24/7 (low-mid) Sch | 6 | 0.9 | 50 | no_default | no_default |  |  | 0.9 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| default | default | Occ 16/7 Constant Sch | Ltg 16/7 Constant Sch | Misc 16/7 Constant Sch | 0 | 0.9 | 100 | no_default | no_default |  |  | no_default | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
Airports
| Baggage | bagg | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 0.76 | 0.76 | 10 | no_default | no_default |  |  | 0.4 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Breakroom | brkm | Occ 16/5 Inter Sch | Ltg 16/5 Inter Sch | Misc 16/5 Inter Sch | 0.5 | 0.5 | 40 | no_default | no_default |  |  | 0.4 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Circulation | circ | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 0.77 | 0.77 | 67 | no_default | no_default |  |  | 0.4 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Conference | conf | Occ 16/5 Inter Sch | Ltg 16/5 Inter Sch | Misc 16/5 Inter Sch | 1 | 0.5 | 20 | no_default | no_default |  |  | 0.4 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Corridor | corr | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 0 | 0.5 | 250 | no_default | no_default |  |  | 0.4 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Counters | coun | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 1.08 | 1.08 | 10 | no_default | no_default |  |  | 0.4 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Custodian | cust | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 0 | 0.5 | 200 | no_default | no_default |  |  | 0.4 | 60 | Heating 60 | 80 | Cooling 80
| Electrical | elec | 24/7 (low) Sch | 24/7 (low) Sch | 24/7 (mid-high) Sch | 5 | 0.5 | 400 | no_default | no_default |  |  | 0 | 60 | Heating 60 | 80 | Cooling 80
| Mechanical | mech | 24/7 (low) Sch | 24/7 (low) Sch | 24/7 (low-mid) Sch | 5 | 0.95 | 400 | no_default | no_default |  |  | 0 | 60 | Heating 60 | 80 | Cooling 80
| Office | offi | Office Occ A Sch | Office Ltg A Sch | Office Eqp A Sch | 0.5 | 0.5 | 200 | no_default | no_default |  |  | 0.2 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Retail | reta | Occ 16/7 Intermit Sch | 24/7 (mid-high) Sch | Misc 16/7 Intermit Sch | 0.5 | 0.9 | 65 | 0.3 | no_default |  |  | no_default | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Seating | seat | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 0.54 | 0.54 | 10 | no_default | no_default |  |  | 0.4 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| ShowerRoom | shrm | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 0 | 0.9 | 100 | no_default | no_default |  |  | 0.5 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Stairs | stai | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 0 | 0.9 | 400 | no_default | no_default |  |  | 0 | 60 | Heating 60 | 999 | Cooling 999
| Storage | stor | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 0 | 0.63 | 200 | no_default | no_default |  |  | 0.4 | 60 | Heating 60 | 80 | Cooling 80
| TeleData | data | 24/7 (low) Sch | 24/7 (low) Sch | 24/7 (mid-high) Sch | 5 | 0.9 | 400 | no_default | no_default |  |  | 0 | 60 | Heating 60 | 80 | Cooling 80
| Toilets | toil | 24/7 (high) Sch | 24/7 (mid-high) Sch | Misc 16/5 Inter Sch | 0 | 0.98 | 40 | no_default | no_default |  |  | 0.5 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| Vestibules | vest | 24/7 (mid-high) Sch | 24/7 (low-mid) Sch | Ltg 16/5 Inter Sch | 0 | 0.9 | 200 | no_default | no_default |  |  | 0 | 60 | Heating 60 | 80 | Cooling 80
| Waiting | wait | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 0.54 | 0.54 | 10 | no_default | no_default |  |  | 0.4 | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch
| default | default | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 24/7 (mid-high) Sch | 0 | 0 | 400 | no_default | no_default |  |  | no_default | 68 | PRJ Heating Sch | 74 | PRJ Cooling Sch